Campus Networking Best Practices  Session 3: Layer 0 Campus Network  Structured Cabling
Campus Networking Best Practices
Session 3: Layer 0
Campus Network
Structured Cabling
Dale Smith
University of Oregon & NSRC
dsmith@uoregon.edu

---
We all have some ugly wiring
We all have some ugly wiring

---
Structured Cabling Systems
Structured Cabling Systems
Only two types of cabling:
  - Unshielded twisted pair copper – provides service to individual computers and between network closets
  - Fiber optic cabling – provides service to buildings and between network closets
Everything is run in a star configuration
Data closet
Core Location
cat5e
Fiber optic

---
Unshielded Twisted Pair Cable
Unshielded Twisted Pair Cable
Run in star configuration from Network Closet location to individual outlets in offices or labs.
Run at least two cables to every outlet – I recommend four if you can afford it.
Run at least six cables between network closets if the distance is less than 90 meters
Question: what type of cable to run? Cat5, cat5e, Cat6, ???

---
What type of UTP
What type of UTP
What speed does each type support?
Strongly recommend category 5e cabling.
Cable Type
Max Speed
Max Distance
Cost Factor
Category 5
100Mbs
100m
1x
Category 5e
1000Mbs
100m
1x
Category 6
1000Mbs
100m
1.3x
Category 6
10,000Mbs
57m
1.3x
Category 6a
10,000Mbs
100m
2x

---
Unshielded Twisted Pair Cable
Labeling is a key to reduce work later

---
Fiber Optic Cabling
Fiber Optic Cabling
Two basic types of fiber
  - Multi Mode limited to 2km @ 100Mbs
  - Single Mode 70km @ virtually unlimited
Multiple types of multi mode
  - 62.5 micron core
  - 50 micron core
Multiple types of single mode
  - Optimized for 1310 and 1550 nm operation
  - Optimized for WDM operation

---
Physics of Fiber
Physics of Fiber

---
What type of Fiber?
What type of Fiber?
Multi mode Fiber
  - 62.5 micron
    - 100baseFX for 2km, optical interface cost $250 USD
    - 1000baseSX for 275m, optical interface cost $250 USD
    - 1000baseLX for 500m, optical interface cost $750 USD
    - 10GbaseSR for 33m, optical interface cost $2000 USD
    - 10GbaseLRM for 220m, optical interface cost $1500 USD (not widely avail)
  - 50 micron laser optimized
    - 100baseFX for 2km, optical interface cost $250 USD
    - 1000baseSX for 550m, optical interface cost $250 USD
    - 1000baseLX for 500m, optical interface cost $750 USD
    - 10GbaseSR for 300m, optical interface cost $2000 USD
    - 10GbaseLRM for 220m, optical interface cost $1500 USD (not widely avail)
Single mode Fiber
  - 100baseFX not supported
  - 1000baseSX not supported
  - 1000baseLX for 5km (most vendors support 10km), cost $750 USD
  - 1000baseLH (not a standard) 70 km with 1550nm lasers, cost $3000 USD
  - 10GbaseLR for 10km, optical interface cost $3000 USD
  - 10GbaseER for 30-40km, optical interface cost $8500 USD

---
Going Fast on Fiber
Going Fast on Fiber
Multi mode Fiber
  - 62.5 micron
    - 1Gbs to 500m
    - 10Gbs to 220m
  - 50 micron laser optimized
    - 1Gbs to 500m
    - 10Gbs to 300m
Single mode Fiber
  - 1Gbs to 70km
  - 10Gbs to 70km

---
Fiber Optic Topology
Fiber Optic Topology
Need to install both Multi and Single Mode
  - Multi mode: either 62.5 or 50 micro is acceptable
  - Single mode: use fiber optimized for 1310/1550nm
Run in star configuration from core network location to individual buildings
Also run in star configuration inside of buildings from main phone closet to other closets
To reduce costs, can run large fiber cable from core to some remote location, then smaller cables from there to surrounding buildings

---
Star Configuration
Star Configuration
Plan for future -- Install enough fiber
  - Minimum: 6 multimode plus 6 single mode from core to each building
  - Minimum: 6 multimode plus 6 single mode from building entrance network closet to every other network closet in the building.
Building to be served
Core network location
Nearby buildings

---
Fiber Optic Topology
Building 1
Network Core Location
fiber
Network Closet 1
fiber
Network Closet 2
fiber
fiber
fiber
fiber
Building 2
Network Closet 3
Building 3
Building 4
fiber
Building 5

---
Construction Hints
Construction Hints
Use outdoor cable between buildings
  - Armored (to protect against rodents)
  - Loose tube
Use indoor cabling inside buildings
  - tight buffer
Standardize on Connectors
  - Multi mode: ST or SC (epoxy or hot melt)
  - Single mode: SC or LC (fusion Splice factory UPC pigtail)

---
Fiber Optic Cable Construction
Fiber Optic Cable Construction
Fiber has bend radius issues

---
More Construction Hints
More Construction Hints
For cable installed in underground conduit:
  - No more than 200m between pull points
  - Reduce distance by 50m for every 90 degrees of bend

---
Fiber Optic Cable Construction
Leave slack loops

---
Putting it all Together
Putting it all Together
Building 1
Network Core Location
fiber
cat5e
Network Closet 1
Cat5e + fiber
Network Closet 2
Cat5e + fiber
fiber
fiber
fiber
Building 2
Network Closet 3
Building 3
cat5e
Building 4
fiber
Building 5

---
How About Going Even Faster?
How About Going Even Faster?
100 Gigabits?
Dispersion becomes your enemy
Even single mode fiber has dispersion
  - Chromatic Dispersion (CD) Even slightly different colors of light travel different speeds
  - Polarization Mode Dispersion (PMD) Slight variations from true roundness causes differently polarized light to travel different distances.

---
The Solution Today is WDM
The Solution Today is WDM
Wave Division Multiplexing (WDM)
  - Provisioning multiple Gigabit or 10 Gigabit using different colors of light
  - Coarse (CWDM)
    - Fewer waves, low cost
    - 1310nm frequency spectrum
    - Not suitable for amplification – short haul (70km)
  - Dense (DWDM) more waves
    - More waves, higher cost
    - 1550nm frequency spectrum
    - Suitable for EDFA amplification – long haul (1000s of km)

---
WDM Simple Single Span
WDM Simple Single Span
Single Fiber
Transmitter
Receiver
Transmitter
Receiver
Transmitter
Receiver
Transmitter
Receiver
Single Fiber
Receiver
Transmitter
Receiver
Transmitter
Receiver
Transmitter
Receiver
Transmitter

---
Optical Add Drop Multiplexor
Optical Add Drop Multiplexor
Transmitter
Receiver
Transmitter
Receiver
Transmitter
Receiver
Transmitter
Receiver

---
Can Build Complex Networks
Can Build Complex Networks
Router
OADM
OADM
OADM
Router
Router
Router
OADM
Fiber
Pair
Fiber
Pair
Fiber
Pair

---
Layer 0 Summary
Layer 0 Summary
Install cabling in star configuration – don’t daisy chain
Install cat5e or cat6a – cat6 is a waste of money if the runs are over 57m
Install both single and multi mode fiber for runs over 300m

---
Thank You
Thank You
Questions