## Slide 1: Structured Network Cabling CIS 399 Day 1, Morning Session 2
Dale Smith
University of Oregon & NSRC
dsmith@uoregon.edu

## Slide 2: We all have some ugly wiring

## Slide 3: Structured Cabling Systems
Only two types of cabling:
  Unshielded twisted pair copper – provides service to individual computers and between network closets
  Fiber optic cabling – provides service to buildings and between network closets
Everything is run in a star configuration
Data closet
Core Location
cat5e
Fiber optic

## Slide 4: Unshielded Twisted Pair Cable
Run in star configuration from Network Closet location to individual outlets in offices or labs.
Run at least two cables to every outlet – I recommend four if you can afford it.
Run at least six cables between network closets if the distance is less than 90 meters
Question: what type of cable to run? Cat5, cat5e, Cat6, ???

## Slide 5: What type of UTP
What speed does each type support?
Cable Type | Max Speed | Max Distance | Cost Factor
Category 5 | 100Mbs | 100m | 1x
Category 5e | 1000Mbs | 100m | 1x
Category 6 | 1000Mbs | 100m | 1.3x
Category 6 | 10,000Mbs | 57m | 1.3x
Category 6a | 10,000Mbs | 100m | 2x
Strongly recommend category 5e cabling.

## Slide 6: Unshielded Twisted Pair Cable
Labeling is a key to reduce work later

## Slide 7: Fiber Optic Cabling
Two basic types of fiber
  Multi Mode limited to 2km @ 100Mbs
  Single Mode 70km @ virtually unlimited
Multiple types of multi mode
  62.5 micron core
  50 micron core
Multiple types of single mode
  Optimized for 1310 and 1550 nm operation
  Optimized for WDM operation
Notes: <number>

## Slide 8: Physics of Fiber

## Slide 9: What type of Fiber?
Multi mode Fiber
  62.5 micron
    100baseFX for 2km, optical interface cost $250 USD
    1000baseSX for 275m, optical interface cost $250 USD
    1000baseLX for 500m, optical interface cost $750 USD
    10GbaseSR for 33m, optical interface cost $2000 USD
    10GbaseLRM for 220m, optical interface cost $1500 USD (not widely avail)
  50 micron laser optimized
    100baseFX for 2km, optical interface cost $250 USD
    1000baseSX for 550m, optical interface cost $250 USD
    1000baseLX for 500m, optical interface cost $750 USD
    10GbaseSR for 300m, optical interface cost $2000 USD
    10GbaseLRM for 220m, optical interface cost $1500 USD (not widely avail)
Single mode Fiber
  100baseFX not supported
  1000baseSX not supported
  1000baseLX for 5km (most vendors support 10km), cost $750 USD
  1000baseLH (not a standard) 70 km with 1550nm lasers, cost $3000 USD
  10GbaseLR for 10km, optical interface cost $3000 USD
  10GbaseER for 30-40km, optical interface cost $8500 USD

## Slide 10: Going Fast on Fiber
Multi mode Fiber
  62.5 micron
    1Gbs to 500m
    10Gbs to 220m
  50 micron laser optimized
    1Gbs to 500m
    10Gbs to 300m
Single mode Fiber
  1Gbs to 70km
  10Gbs to 70km

## Slide 11: How About Going Even Faster?
Dispersion becomes your enemy at 10Gbs and above (40 and 100Gbs very hard)
Even single mode fiber has dispersion
  Chromatic Dispersion (CD) Even slightly different colors of light travel different speeds
  Polarization Mode Dispersion (PMD) Slight variations from true roundness causes differently polarized light to travel different distances.

## Slide 12: The Solution Today is WDM
Wave Division Multiplexing (WDM)
  Provisioning multiple Gigabit or 10 Gigabit using different colors of light
  Coarse (CWDM)
    Fewer waves, low cost
    1310nm frequency spectrum
    Not suitable for amplification – short haul (70km)
  Dense (DWDM) more waves
    More waves, higher cost
    1550nm frequency spectrum
    Suitable for EDFA amplification – long haul (1000s of km)

## Slide 13: WDM Simple Single Span
Transmitter
Transmitter
Transmitter
Transmitter
Receiver
Receiver
Receiver
Receiver
Single Fiber
Receiver
Receiver
Receiver
Receiver
Transmitter
Transmitter
Transmitter
Transmitter
Single Fiber

## Slide 14: Optical Add Drop Multiplexor
Transmitter
Transmitter
Transmitter
Transmitter
Receiver
Receiver
Receiver
Receiver

## Slide 15: Can Build Complex Networks
OADM
OADM
OADM
OADM
Fiber
Pair
Fiber
Pair
Fiber
Pair
University
University
University
NREN

## Slide 16: Varying Service Models
Internet Service Provider (ISP) provides Internet and circuit to your site
ISP is different from provider of circuits
Best situation when you have choices in both ISP and provider of telecom or fiber services
  Competition is the key

## Slide 17: Fiber Optic Topology
Fiber Types
  Multi mode: don’t bother if run is over 200M
  Single mode: use fiber optimized for 1310/1550nm
Run in star configuration from core network location to individual buildings
Also run in star configuration inside of buildings from main phone closet to other closets
To reduce costs, can run large fiber cable from core to some remote location, then smaller cables from there to surrounding buildings

## Slide 18: Star Configuration
Plan for future -- Install enough fiber
  Minimum: 6 multimode plus 6 single mode from core to each building
  Minimum: 6 multimode plus 6 single mode from building entrance network closet to every other network closet in the building.
Core network location
Building to be served
Nearby buildings

## Slide 19: Fiber Optic Topology
Network Core Location
Network Closet 1
Building 3
Network Closet 2
Building 1
Network Closet 3
Building 5
Building 4
Building 2
fiber
fiber
fiber
fiber
fiber
fiber
fiber

## Slide 20: Construction Hints
Use outdoor cable between buildings
  Armored (to protect against rodents)
  Loose tube
Use indoor cabling inside buildings
  tight buffer
Standardize on Connectors
  Multi mode: ST or SC (epoxy or hot melt)
  Single mode: SC or LC (fusion splice factory pigtails, however hand polish is OK if done properly)

## Slide 21: Fiber Optic Cable Construction
Fiber has bend radius issues

## Slide 22: More Construction Hints
For cable installed in underground conduit:
  No more than 200m between pull points
  Reduce distance by 50m for every 90 degrees of bend

## Slide 23: Fiber Optic Cable Construction
Leave slack loops

## Slide 24: Putting it all Together
Network Core Location
Network Closet 1
Building 3
Network Closet 2
Building 1
Network Closet 3
Building 5
Building 4
Building 2
cat5e
fiber
cat5e
Cat5e + fiber
Cat5e + fiber
fiber
fiber
fiber
fiber

## Slide 25: Structured Cabling Summary
Install cabling in star configuration – don’t daisy chain
Install cat5e or cat6a – cat6 is a waste of money if the runs are over 57m
If runs are under 200M, then multi mode is OK
Must do single mode if runs over 200M

## Slide 26: Thank You
Questions